Cyclic interrupt(OB30):

"Sim".Level := "LevelIn" * 20.0;                       // level 0..100

// operator control — scene buttons OR HMI buttons (latched)

IF "StartBtn" OR "HMI_Start" THEN

"Running" := TRUE;

END_IF;

IF NOT "StopBtn" OR "HMI_Stop" THEN

"Running" := FALSE;

END_IF;

IF "ResetBtn" THEN

"Running" := FALSE;

END_IF;

// process runs ONLY when Running

IF "Running" THEN

IF "Sim".Level < 30.0 THEN

"FillValve" := 100.0;

END_IF;

IF "Sim".Level > 70.0 THEN

"FillValve" := 0.0;

END_IF;

"DischargeValve" := 40.0;

ELSE

"FillValve" := 0.0;

"DischargeValve" := 0.0;                           // Stop = valves closed, tank holds

END_IF;

// indicator lights (scene lamps)

"StartLight" := "Running";

"StopLight" := NOT "Running";

"ResetLight" := "ResetBtn";

Default tag table:

| Tag | Data Type | Address | Flag 1 | Flag 2 | Flag 3 | Flag 4 |
| --- | --- | --- | --- | --- | --- | --- |
| Level_Meter | Int | %IW100 | False | True | True | True |
| Flow_Meter | Int | %IW102 | False | True | True | True |
| Setpoint | Int | %IW104 | False | True | True | True |
| Warning_Light | Bool | %Q0.3 | False | True | True | True |
| Alarm(1) | Bool | %Q0.4 | False | True | True | True |
| Fill | Int | %QW100 | False | True | True | True |
| Discharge(1) | Int | %QW102 | False | True | True | True |
| LevelIn | Real | %ID100 | False | True | True | True |
| FillValve | Real | %QD100 | False | True | True | True |
| DischargeValve | Real | %QD104 | False | True | True | True |
| StartBtn | Bool | %I10.0 | False | True | True | True |
| ResetBtn | Bool | %I10.1 | False | True | True | True |
| StopBtn | Bool | %I10.2 | False | True | True | True |
| StartLight | Bool | %Q0.0 | False | True | True | True |
| ResetLight | Bool | %Q0.1 | False | True | True | True |
| StopLight | Bool | %Q0.2 | False | True | True | True |
| Running | Bool | %M0.0 | False | True | True | True |
| HMI_Start | Bool | %M0.1 | False | True | True | True |
| HMI_Stop | Bool | %M0.2 | False | True | True | True |

Factory IO config:

## PLC Configuration

- Auto connect: Disabled (unchecked)

- Model: S7-1200

- Host: 192.168.2.10

- Network adapter: Intel(R) Ethernet Connection (18) I219-LM #2

## I/O Configuration

- Numerical Data Type: DWORD

## I/O Points

| I/O Type | Offset | Count |
| --- | --- | --- |
| Bool Inputs | 10 | 4 |
| Bool Outputs | 0 | 3 |
| DWORD Inputs | 100 | 3 |
| DWORD Outputs | 100 | 4 |

On dell 1:
The command block when ran first gave this single line output:
Start=0 Reset=0 Stop=1 | Running=1 | LevelIn=1.66 Fill=100.0 Disch=40.0 DB7=33.20

And then on second run:
Traceback (most recent call last):

File "/usr/local/lib/python3.12/dist-packages/snap7/connection.py", line 248, in _tcp_connect

self.socket.connect((self.host, self.port))

TimeoutError: timed out

During handling of the above exception, another exception occurred:

Traceback (most recent call last):

File "/tmp/rd2.py", line 8, in <module>

try: c.connect('192.168.2.10',0,1); break

^^^^^^^^^^^^^^^^^^^^^^^^^^^^^

File "/usr/local/lib/python3.12/dist-packages/snap7/client.py", line 592, in connect

self.connection.connect()

File "/usr/local/lib/python3.12/dist-packages/snap7/connection.py", line 137, in connect

self._tcp_connect()

File "/usr/local/lib/python3.12/dist-packages/snap7/connection.py", line 251, in _tcp_connect

raise S7ConnectionError(f"TCP connection failed: {e}")

snap7.error.S7ConnectionError: TCP connection failed: timed out

And also its seen in dashboard the CARS-Remediation attacking PLC1